## Slide 1: Medical Gases
Presenter
Click here to insert date

## Slide 2: Background
Medical gases have the potential for creating hazardous working environments
When medical gases are not handled and used properly, there is the potential for injuries or accidents to occur
Injuries may result from—
the displacement of oxygen from a leaking gas cylinder
fires or injuries caused by flammable gas ignition
inhalation of a toxic or asphyxiating gas
flying objects accelerated by an explosion or pressure release
Some examples of medical gases include medical air, USP; oxygen USP; helium USP; nitrogen NF; and mixtures of these gases
Notes: USP – United States Pharmacopeia
NF – National Formulary

## Slide 3: Lesson Objectives
Describe the hazards associated with medical gases
Discuss safe handling and use guidelines
Explain proper storage procedures
Notes: At the end of this presentation students should be able to ….

## Slide 4: Definitions
Asphyxiant—a gas that has the ability to cause suffocation in an enclosed workspace by displacing breathable air.
Compressed gas—any material that is normally a gas which is placed under pressure or chilled, and contained by a cylinder
Corrosive—a gas that can cause severe burns to skin and other human tissues such as the eye or lung, and can attack clothes and other materials including metal
Cryogenic—liquefied gases that are kept in their liquid state at very low temperatures (below −292⁰F)
Flammable—a material that will burn or catch on fire easily at normal temperatures below 100⁰F
Inert—a gas that does not usually react with other things
Notes: The OSHA considers atmospheres to be oxygen deficient when the oxygen content in air falls below 19.5%. Oxygen deficient atmospheres are considered to be immediately dangerous to life and health
Liquid nitrogen (Dermatology) is an asphyxiant and a cryogen.
Common corrosive gases include ammonia, hydrogen chloride, chlorine and methylamine.
Acetylene (used in welding) and hydrogen are flammable gases.
Helium, argon, neon, xenon, krypton, radon (noble gases) are inert gases.

## Slide 5: More Definitions
Gas—a form of matter that does not have a defined shape or volume. Gases can consist of a single element, such as hydrogen gas (H2), or may be a compound, such as carbon dioxide (CO2), or a mixture of several gases, such as air. Gases expand to fill the space they are given
Oxidizer—a gas that does not usually burn itself, but will either help the fire by providing more oxygen or they may cause materials that normally do not burn to suddenly catch on fire (spontaneous combustion)
Pyrophoric—a material that ignites instantly upon exposure to oxygen
Reactive—a gas that had the potential to vigorously polymerize, decompose, condense, or become self-reactive under conditions of shock, pressure, temperature, light, or contact with another material
Toxic—Capable of causing injury or death, especially by chemical means; poisonous
Notes: Air, helium, nitrogen, freon, carbon dioxide, water vapor, hydrogen, natural gas, propane, oxygen, ozone, and hydrogen sulfide are some examples of gases.
Oxygen and nitrous oxide are examples of oxidizers.
Phosphine is a pyrophoric gas.
Common dangerously reactive gases are acetylene, 1,3-butadiene, methyl acetylene, vinyl chloride, tetrafluoroethylene and vinyl fluoride. Reactions may be violent, resulting in fire or explosion. Some dangerously reactive gases have other chemicals, called inhibitors, added to prevent these hazardous reactions.
Chlorine is an example of a toxic gas
Common dangerously reactive gases are acetylene, 1,3-butadiene, methyl acetylene, vinyl chloride, tetrafluoroethylene and vinyl fluoride.

## Slide 6: Content Identification/Product Labeling
Good safety begins with the proper identification of the gas cylinder’s contents
All cylinders must have a legible label that identifies their contents and gives precautionary warnings to users who are responsible for handling them and for connecting them for use
The color of the cylinder alone may not be used to identify a cylinder’s contents
Cylinders that are not properly labeled should be set apart for return to the gas supplier
Notes: For small groups, consider having a properly secured cylinder available so students can practice reading the label. Inserting a picture of a label in this presentation is another option.

## Slide 7: Physical Hazards
All compressed gases are hazardous because of the high pressures inside the cylinders
Gas can be released deliberately by opening the cylinder valve, or accidentally from a broken or leaking valve or safety device
Even at a relatively low pressure, gas can flow rapidly from an open or leaking cylinder
There have been many cases in which damaged cylinders have become uncontrolled rockets or pinwheels and have caused severe injury and damage. This danger has occurred when unsecured, uncapped cylinders were knocked over causing the cylinder valve to break and high pressure gas to escape rapidly
Most cylinder valves are designed to break at a point with an opening of about 0.75 cm (0.3 inches). This design limits the rate of gas release and reduces cylinder velocity. This limit may prevent larger, heavier cylinders from "rocketing" although smaller or lighter cylinders might take off
Notes: Think of how an inflated balloon reacts when the air is suddenly released from its mouth

## Slide 8: Health Hazards
Compressed gases may be flammable, corrosive, toxic, reactive, oxidizers, cryogenic, pyrophoric, or cause asphyxiation
Some compressed gases may have a combination of hazards, for example liquid oxygen combines the oxidizer hazard with the cryogenic hazard
Detailed information regarding the physical and chemical properties, specific handling, safety precautions, physiological effects on humans and emergency procedures are covered in the gas suppliers safety data sheets (SDS)

## Slide 9: Receipt DO’s
Remove any paper wrapping before placing cylinders in service so the label is clearly visible
Inspect cylinders for proper labeling, color-coding, bulges, or damage
Return unused cylinders to the supplier if they are damaged, or improperly color-coded, and if they do not have a label, the label is unreadable, or if the label does not correctly identify the gas contained in the cylinder
Test medical oxygen upon receipt to verify that the cylinders contain medical grade oxygen, annotate DD Forms 1191, Warning Tag for Medical Oxygen Equipment, with test results and attach the forms to the cylinders
Notes: Oxygen testing is further explained in a later slide.

## Slide 10: Safe Handling DO’s
Allow only experienced and trained workers to handle compressed gas cylinders
Read and understand all warning and precautionary information on the cylinders’ labels
Identify the gas content by reading the label before use
Attach “in use” cylinders to a stand or to medical equipment designed to hold medical gas equipment
Mark empty cylinders to avoid confusion and delay if a full cylinder is needed quickly
Prevent sparks or flame from coming into contact with cylinders and equipment
Notes: Per DA Supple Bulletin (SB) 8-75-11, All personnel handling medical gases in cylinders must be properly trained on transporting, handling, storing and the hazardous of working with medical gases. Initial training must be conducted, and refresher training every three years. Training must be documented and documentation retained for duration of employment.
Cylinders must be marked to indicate the amount of gas contained within. This is critical so that nurses can quickly pick up a full oxygen cylinder when needed. Perforated tags are one way to accomplish this. Marking empty cylinders with “MT and date” with chalk or posting signage on the wall behind the storage rack or on the storage rack are alternate means to accomplish this requirement. Consider inserting a picture or use an actual tag or cylinder.

## Slide 11: Safe Handling DO’s
Leave valve protection caps in place (if provided) until cylinders are secured and connected for use (Note: Style E and smaller cylinders are not equipped with valve protection caps and are vulnerable to valve damage if dropped in an inverted position)
Some types of gas cylinders have valve outlet caps and plugs that form a gas-tight seal. Keep the device on the valve outlet except when containers are secured and connected to dispensing equipment
Keep valves closed when the gas is not being used. Closing the valve isolates the cylinder’s contents from the surrounding atmosphere and prevents corrosion and contamination of the valve
Close valves before returning empty cylinders to storage and replace the valve protective caps (if provided) before moving cylinders
Handle empty cylinders as carefully as full ones; residual pressure can be dangerous
Notes: Consider inserting pictures.

## Slide 12: Still More Safe Handling DO’s
Follow instructions for using regulators—
Open valves slowly
Slightly open the valve for an instant to clear the opening of possible dust and dirt after removing the valve protection cap
Stand so that the valve outlet is pointed away from yourself and others in the work area when opening the valve
Use wrenches or tools provided by the supplier to open the valves
Make sure that the threads on regulator-to-cylinder-valve connections or the pin-indexing devices on the yoke-to-cylinder-valve connections are properly mated
Check to make sure connections are tight to prevent leakage
Open the cylinder valve completely when the cylinder is in use
Close the cylinder valves and relieve pressure in the regulator before disconnecting the regulator
Keep valves closed unless gas is being dispensed
Notes: Consider conducting a demonstration showing proper technique for installing regulators or showing a video such as this one found on youtube at https://www.youtube.com/watch?v=DcW04sY8S0w

## Slide 13: Safe Handling DONT’s
Use cylinders for any purpose other than to supply the contained gas
Use or store ferromagnetic cylinders near the magnetic resonance imager (MRI)
Let oil, grease, or other combustible materials come in contact with containers, valves, regulators, gauges, hoses, and fittings
Lubricate valves, regulators, gauges, or fittings with oil or any other combustible material
Handle cylinders or apparatus with oily hands or gloves
Use an open flame to detect gas leaks
Interchange regulators or other appliances used with one gas with similar equipment used with other gases

## Slide 14: More Safe Handling DONT’s
Deface or remove any markings used to identify the cylinder’s contents
Subject any part of a compressed gas cylinder to temperatures above 125⁰F
Add adapters to existing connections or modify or replace existing connections
Change, modify, tamper with, or obstruct the discharge ports of pressure relief devices
Place cylinders where they can become part of an electric circuit
Repaint cylinders
Use cylinders as rollers or supports

## Slide 15: Safe Moving
DO
Use valve protection caps to protect the valves when moving cylinders
Always secure cylinders to a suitable hand truck when transporting them within the facility
DO NOT
Drop or let cylinders strike against each other
Roll, drag, or slide cylinders
Notes: Consider inserting pictures.

## Slide 16: Safe Bulk Storage DO’s
Verify that the bulk compressed gas storage location is protected from unauthorized access and does not obstruct egress from the facility
Verify the bulk storage room is constructed of non-combustible or limited combustible materials (concrete or sheet rock respectively for example) and either partially or fully devoted for gas cylinder storage
Post a sign (readable from five feet) identifying it as a gas storage room, including the following warning—CAUTION; OXIDIZING GASES STORED WITHIN; NO SMOKING
Physically separate gases stored within the room by type or hazard class of the gas
Maintain a minimum distance of 20 feet between oxidizing gases and combustible materials (Note: the minimum distance to combustible material may be reduced to 5 feet when the room is protected by an automatic fire sprinkler system)
Notes: Consider inserting pictures.

## Slide 17: More Safe Bulk Storage DO’s
Physically separate full and empty cylinders
Rotate cylinders so that they are used in the order that they are received (first in – first out)
Secure cylinders with straps or chains or place them in racks or on shelving cylinders to prevent them from falling
Notify the supplier if a cylinder is noticeably corroded, dented, cut, damaged, or involved in an accident, and follow the supplier’s instructions for remedying the situation
Visually inspect stored cylinders on a routine basis, or at least weekly, for any indication of leakage or problems
Notes: Consider inserting pictures.

## Slide 18: Emergency Procedures
An emergency is any actual or potential release of a gas that cannot be stopped by closing the cylinder valve
Federal law requires that all facilities using compressed gases develop emergency response plans based on the potential hazards of the gases being stored and used
Practice implementing emergency response plans so that all contingencies are covered
Assign responsibilities and lines of authority for responding to emergencies
Coordinate emergency response with the local fire department and inform them of the gases in use so they can be prepared with the needed expertise and equipment
Develop first aid and medical response procedures for potential injuries

## Slide 19: Oxygen
Every oxygen cylinder must have a DD Form 1191, Warning Tag for Medical Oxygen Equipment, attached to it showing the oxygen purity test results, date tested, tester’s initials
Store no more than 12 size E oxygen cylinders or 1 size H and 2 size E cylinders in a single smoke compartment (in use and empty cylinders are not included in the count)
Additional cylinders may be stored within the smoke compartment in a CLEAN, well-ventilated, storage room that is protected with 1-hour fire rated walls and 45-minute fire rated doors
Notes: The Army requires testing of medical oxygen when it is received from the supplier to verify that it is at least 99 percent pure by volume. Cylinders that do not have a DD Form 1191 should be sent back to Logistics to be tested. Consider inserting pictures.
Testing is required to prevent medical gas mix-ups. The FDA has received reports from hospitals and nursing homes involving 7 deaths and 15 injuries to patients who were thought to be receiving medical grade oxygen, but were receiving a different gas (e.g., nitrogen) that had been mistakenly connected to the oxygen supply system. Texting the oxygen will reduce the chance of error and subsequent harm to patients.

## Slide 20: Liquid Nitrogen
Nitrogen has no warning properties—it is colorless and odorless
Liquid nitrogen is a cryogen (boiling point is -320⁰F at 1 atm)
Store liquid nitrogen containers in a CLEAN, ventilated storage room that is protected with 1-hour fire rated walls and 45-minute fire rated doors. The temperature should stay constant
Store containers away from air intakes, high traffic areas, floor drains, and other underground openings
Do not plug, remove, or tamper with any pressure relief device
Keep all valves closed and outlet caps in place when not in use, and do not leave liquid containers open to the atmosphere for extended periods
Notes: The volume expansion rate of nitrogen is 700 to 1 when warmed to room temperature.

## Slide 21: More Liquid Nitrogen
Store, handle, and transport cryogenic containers in the upright position
When moving, never tip, slide or roll containers on their side
Use a suitable hand truck for moving containers, and use a nylon strap to secure the container to the hand truck
Move larger containers by pushing, not pulling
Wear appropriate personal protective equipment when transferring liquid nitrogen to smaller containers (safety goggles or glasses with side shields, a face shield, and cryogenic gloves) along with sturdy shoes and long pants without cuffs. Pants should be left outside the work boots or shoes
Use only transfer equipment designed for use with cryogenic liquids
Notes: Consider inserting pictures of the appropriate PPE or providing examples that students and observe up close.

## Slide 22: Still More Liquid Nitrogen
Perform transfer operations slowly to minimize boiling and splashing
Discontinue use and contact the supplier if there is any difficulty in operating the container valve or container connections
Contact the supplier if a restriction results from freezing moisture or foreign material present in openings and vents (restrictions and blockages may result in dangerous over-pressurization)
Do not attempt to remove the restriction without proper instructions; if possible, move the container to a remote location
Seek prompt medical assistance as soon as possible following a cold-contact burn

## Slide 23: Recap
Medical gas hazards include oxygen displacement, fires, explosions, and toxic gas exposures, as well as the physical hazards associated with high pressure systems
Personnel who handle medical gases must be well-trained and knowledgeable of the gases’ physical and health hazards and safe work practices
Special storage, use, and handling precautions are necessary to control medical gas hazards
Employers must evaluate medical gas hazards and have an emergency response plan that defines the procedures and responsibilities to address such emergencies
The Joint Commission and OSHA can cite hospitals and clinics for improperly handling medical gas cylinders
Notes: Compressed Gas Checklist
Location:
Date of inspection:
Signature of inspector:
1. Are cylinders stored in upright positions and immobilized by chains or other means to prevent them from being knocked over? [CGA 3.4.4 and 29 CFR 1910.101(b)]
2. Are cylinders stored away from highly flammable substances such as oil, gasoline, or waste? [CGA 3.3.6]
3. Are cylinders stored away from electrical connections, gas flames or other sources of ignition, and substances such as flammable solvents and combustible waste material? [CGA 3.5.1]
4. Are flammable gases separated from oxidizing gases in storage areas? [CGA 3.3.3]
5. Are oxygen and fuel gas cylinders separated by a minimum of 20 feet when in storage? [CGA 3.5.3]
Note: A fire-resistant partition between the cylinders can also be used.
6. Are storage rooms for cylinders dry, cool, and well- ventilated? [CGA 3.3.5]
Note: The storage rooms should be fire resistant and the storage should not be in subsurface locations. Cylinders should be stored in secure areas at temperatures below 125ºF, away from radiators or other sources of heat.
7. Are cylinders stored away from incompatibles, excessive heat, continuous dampness, salt or other corrosive chemicals, and any areas that may subject them to damage? [CGA 3.3.7 and 29 CFR 1910.101(b)]
Note: Rusting will damage the cylinder and may cause the valve protection cap to stick.
8. Is the storage area permanently posted with the names of the gases stored in the cylinders? [CGA 3.3.2 and 29 CFR 1910.101(b)]
9. Do all compressed gas cylinders have their contents and precautionary labeling clearly marked on their exteriors? [29 CFR 1910.101(b)]
10. Are all compressed gas cylinder valve covers in place when cylinders are not in use? [29 CFR 1910.101(b)]
11. Are all compressed gas cylinders stored so they do not interfere with exit paths? [29 CFR 1910.101(b)]
12. Are all compressed gas cylinders subjected to periodic hydrostatic testing and interior inspection? [29 CFR 1910.101(a)]
Note: This is normally done by the supplier.
13. Do all compressed gas cylinders have safety pressure relief valves? [29 CFR 1910.101(c)]
14. Are cylinders always maintained at temperatures below 125ºF? [CGA 3.1.12]
15. Are safety relief devices in the valve or on the cylinder free from any indication of tampering? [CGA 3.1.14]
16. Is repair or alteration to the cylinder, valve, or safety relief devices prohibited? [CGA 3.1.15]
Note: All alterations and repairs to the cylinder and valve must be made by the compressed gas vendor. Modification of safety relief devices beyond the tank or regulator should only be made by a competent person appointed by management.
17. Is painting cylinders without authorization by the owner prohibited? [CGA 3.1.20]
Note: Often color codes are used to help designate cylinders. Arbitrary paint is not recommended.
18. Are charged or full cylinders labeled and stored away from empty cylinders? [CGA 3.3.4 and 29 CFR 1910.101(b)]
19. Is the bottom of the cylinder protected from the ground to prevent rusting? [CGA 3.3.9]
20. Are all compressed gas cylinders regularly inspected for corrosion, pitting, cuts, gouges, digs, bulges, neck defects and general distortion? [29 CFR 1910.101(a)]
21. Are cylinder valves closed at all times, except when the valve is in use? [CGA 3.1.15]
Note: Regulator diaphragms have failed, and unwanted gas was delivered to an area or apparatus, causing safety and health problems.
22. Are compressed gas cylinders always moved, even short distances, by a suitable hand truck? [CGA 3.2.6]
Note: They must never be dragged across the floor. Serious accidents have occurred when a cylinder with a regulator in place was improperly moved. The cylinder fell, causing the regulator to shear off, and the cylinder rocketed through several brick walls.
23. Is using wrenches or other tools for opening and closing valves prohibited? [CGA 3.4.9]
Note: Hammering on valve wheels to open them should be strictly prohibited. For valves that are hard to open, contact the supplier for instruction.
24. Are suitable pressure regulating devices in use whenever the gas is emitted to systems with pressure-rated limitations lower than the cylinder pressure? [CGA 3.4.5]
25. Are all compressed gas cylinder connections such as pressure regulators, manifolds, hoses, gauges, and relief valves checked for integrity and tightness? [29 CFR 1910.101(a)]
26. Are all compressed gas cylinders regularly subjected to leak detection using an approved leak detecting liquid? [29 CFR 1910.101(a)]
Note: Ordinary soap solution may contain oils that are unsafe when used with oxygen cylinders. Leak detection liquids are available from commercial welding supply houses.
27. Is an approved leak-detection liquid used to detect flammable gas leaks ? [CGA 3.5.2]
Note: A flame should never be used.
28. Are procedures established for when a compressed gas cylinder leak cannot be remedied by simply tightening the valve? [CGA 3.1.6]
  The procedures should include the following:
  1. Attach tag to the cylinder stating it is unserviceable.
  2. Remove cylinder to a well ventilated out of doors location.
  3. If the gas is flammable or toxic, place an appropriate sign at the cylinder warning of these hazards.
  4. Notify the gas supplier and follow his/her instructions as to the return of the cylinder.
29. Are employees prohibited from using compressed gases (air) to clean clothing or work surfaces? [29 CFR 1910.101(b)]
30. Are compressed gases only handled by experienced and properly trained people? [CGA 3.4.1]

## Slide 24: Local Procedures
The medical gas safety standing operating procedures are available at (fill in the blank) Questions regarding medical gases should be directed to (fill in the blank)

## Slide 25: Quiz: Question 1
True or False
The primary physical hazard associated with medical gases is pressure.
Notes: Answer: True

## Slide 26: Quiz: Question 2
Select the best answer
An oxidizing gas—
ignites instantly upon exposure to oxygen
does not usually burn itself, but will either help the fire by providing more oxygen or they may cause materials that normally do not burn to suddenly catch on fire (spontaneous combustion)
has the potential to vigorously polymerize, decompose, condense, or become self-reactive under conditions of shock, pressure, temperature
none of the above
Notes: Answer: b

## Slide 27: Quiz: Question 3
True or False
The best way to identify the contents of a medical gas cylinder is to read the label.
Notes: Answer: True

## Slide 28: Quiz: Question 4
Select the best answer
Cylinders should be returned to the supplier when they are—
damaged
improperly color-coded
the label does not correctly identify the gas contained in the cylinder
All of the above
Notes: Answer: d

## Slide 29: Quiz: Question 5
True or False
Workers handling medical gases must attend initial training and annual refresher training.
Notes: Answer: False – initial and every three years

## Slide 30: Quiz: Question 6
True or False
A minimum distance of 20 feet between oxidizing gases from combustible materials must be maintained except when the cylinders are stored in a room with fire rated construction.
Notes: Answer: False – when they are stored in rooms protected with an automatic sprinkler system

## Slide 31: Quiz: Question 7
Fill in the Blank
No more than _____ size E oxygen cylinders or _____ size H and _____ size E cylinders may be outside of a protected storage room in a single smoke compartment.
Notes: Answer: 12/1/2

## Slide 32: Quiz: Question 8
True or False
Examples of medical gases include medical air, USP; oxygen USP; helium USP; nitrogen NF; and mixtures of these gases.
Notes: Answer: True

## Slide 33: Quiz: Question 9
True or False
Consistent with good infection control practices, store medical gas cylinders in soiled utility rooms since they are being used for patient care.
Notes: Answer: False – should be stored in a clean area

## Slide 34: Quiz: Question 10
True or False
Ferromagnetic cylinders may be used or stored near the magnetic resonance imager (MRI)
Notes: Answer: False
A six year old boy undergoing an MRI (Magnetic Resonance Imaging) scan was killed by a ferromagnetic oxygen tank that was pulled into the MR scanner at a New York-area hospital when the machine's powerful magnetic field jerked a metal oxygen tank across the room, crushing the child's head. The force of the device's 10-ton magnet is about 30,000 times as powerful as Earth's magnetic field, and 200 times stronger than a common refrigerator magnet. The canister fractured the skull and injured the brain of the young patient, Michael Colombini, of Croton-On-Hudson, N.Y., during the procedure Friday. He died of the injuries on Sunday, the hospital said.

## Slide 35: Learn More
Army Regulation 700-68, Storage and Handling of Liquefied and Gaseous Compressed Gasses
Compressed Gas Association (CGA) P-1, Safe Handling of Compressed Gases in Containers
CGA P-2, Characteristics and Safe Handling of Medical Gases
CGA P-2.7, Guide for the Safe Storage, Handling, and Use of Small Portable Liquid Oxygen Systems in Healthcare Facilities
CGA P-12, Safe Handling of Cryogenic Liquids
CGA P-30, Portable Cryogenic Liquid Containers – Use, Care, and Disposal
NFPA 99-2015, Healthcare Facilities Code
DA Supply Bulletin, 8-75-11, Army Medical Department Supply Information
National Fire Protection (NFPA) 99, Health Care Facilities Code
Occupational Safety and Health Administration (OSHA), 29 Code of Federal Regulations (CFR) 1910.101, Compressed Gases (General Requirements)