- ENVIRONMENT OF CARE

- FIRE SAFETY MANAGEMENT PLAN

- JANUARY 2013

1.  	Goal

2.  	Objectives

3.  	Scope

4.	Responsibilities

5.  	Fire Safety Elements of Performance

a.	Fire Safety Management Plan

b.	Risk Assessments

c.	Risk Assessment Process

d. 	Minimizing Potential for Harm

e.	Patient Smoking Policy

f.	Unobstructed Egress

g.	Fire Response Plan

h.	Staff Roles

i.	Fire Drills

j.	Preventive Maintenance for Fire Safety 			Equipment and Building Features

k.	Life Safety Code Compliance

l.	Interim Life Safety Measures

m.	Orientation and Annual Refresher

Education and Training Program

n.	Information Collection and Evaluation

System

(1)	Reporting and Investigating

Accidents, Injuries, Property 					Damage, Problems, Failures, & Use Errors

(2)	Annual Evaluation

(3)	Safety/EC Committee

(4) 	Performance Improvement 				Activities

1.	Goal.  This management plan describes the framework used to manage fire risks and continuously improve safety performance.  The scope and objectives are consistent with the Command’s values, vision, and mission in providing quality healthcare to Soldiers, retirees, and their families.

2.	Objectives.  The following objectives will prevent human injuries, maintain a physical environment free of physical hazards, and safeguard Army property.

a.	Effectively manage fire safety risks by using best industry practices

b.	Optimize resources by using efficient fire safety processes and lifecycle management of facilities

c.	Improve staff performance through effective fire safety education and training

d.	Improve staff and patient satisfaction by providing a safe physical environment

3.	Scope.  This management plan applies to this Military Treatment Facility (MTF), and all subordinate MTFs to include (LIST ALL CLINICS AND SATELLITE LOCATIONS SERVED BY THE MTF AND COVERED UNDER THIS PLAN).

4.  	Responsibilities.

a. 	The Safety Manager and the Facility Manager are responsible for developing, implementing, and monitoring this plan.  The Safety Manager focuses on the human aspects of fire safety such as safe work practices and emergency response and evacuation.  The Facility Manager focuses on the physical aspects of fire safety such as operability of fire safety equipment and the design, construction, and maintenance of buildings.

b.	The Organization Chart in Appendix A shows the primary officers, departments, and services that provide input into the development, implementation, and maintenance of the Fire Safety Management Plan.

c.	Service and department chiefs develop and implement department-specific fire safety standing operating procedures (SOPs) and carry-out the MTF-wide fire safety policies and regulations.

d.	All staff, personnel, and volunteers obey fire safety rules, know department-specific and facility-wide fire response procedures, and participate in fire exit drills.

5.  Fire Safety Elements of Performance.  The Reference Crosswalk in Appendix B lists the corresponding policies, regulations, SOPs, systems, and databases pertaining to each of these standards:

a.	Fire Safety Management Plan.  This plan is based on a plan, teach, implement, respond, monitor, and improve framework and it addresses two important aspects of fire safety:  prevention and emergency response.  Both are essential for maintaining a safe Environment of Care (EC)/Physical Environment (PE).

b.	Risk Assessments.

(1) 	The MTF uses a risk identification and assessment process to evaluate the impact of buildings, grounds, equipment, occupants, processes, and systems on the safety and health of patients, staff, and other people coming into the facility.  Management and staff are responsible for implementing composite risk management.

(2) 	Both proactive risk assessments (e.g., internal performance improvement data; staff, patient, and family feedback; environmental monitoring; results of failure mode and effects analyses; governmental regulation reviews; association, society, professional literature reviews; preventive maintenance; design reviews; etc.) and reactive risk assessments (e.g., incident and accident investigation reports, utility or equipment failure investigations, fire and emergency investigations, root causes analyses, etc.) are used to identify trends for which corrective action is needed.

(3) 	In addition, the risk assessment process is used to manage “gray areas,” that do not have a clear resolution.  An example of a “gray area” is deciding the best way to secure sharps in the Emergency Room.  “Gray area” issues are brought to the Safety/EC Committee for discussion and resolution.

c.	Risk Assessment Process.  The Safety Manager assigns a risk assessment code to all safety and health hazards and tracks their abatement on a worst-first basis.  The Safety and Facilities Managers develop and implement interim safety measures to manage risk and minimize potential for harm to patients, staff, and visitors when serious LSC hazards cannot be immediately abated and during construction in occupied buildings.

d.	Minimizing Potential for Harm.  Strategies used by the MTF to protect patients, personnel, visitors, and property from fire and products of combustion include, but are not limited to the following:

(1) 	Compliance with NFPA 101, LSC and other NFPA standards referenced by the LSC; 29 CFR 1910.38; Employee Emergency Plans and Fire Prevention Plans; Army Regulations; and local fire protection codes

(2) 	Testing and maintenance programs for fire protection systems and safety equipment

(3) 	Continuous identification and correction of life safety deficiencies through a building maintenance program, life safety assessment program, and plans for improvement

(4) 	Implementation of interim life safety measures (ILSM) during construction and when significant life safety deficiencies exist

(5) 	Procurement of flame resistant, bedding, draperies and other curtains, furnishings, decorations, and other equipment

(6) 	Development and implementation of effective fire prevention and emergency response plans

(7) 	Training and education programs that address assignment of specific duties, use and function of fire alarm systems, transmission of alarms, containment of smoke and fire, fire extinguishment, transfer to areas refuge, and preparation for building evacuation

(8) 	Conduct and evaluation of periodic fire drills to reinforce fire safety training

(9) 	Enforcement of the MTF’s No Smoking Policy

e.	Patient Smoking Policy.  Patients are permitted to smoke only in designated outdoor smoking areas.  All patients are strongly discouraged from smoking.

f.	Unobstructed Egress.  All means of egress (stair, aisles and corridors, doors, etc.) are continuously maintained free from all obstructions or impediments to allow for full instant use in the case of fire or other emergency.  The Safety and Facility Managers routinely monitor all means of egress and work with supervisors to resolve non-compliance issues.

g.	Fire Response Plan.  The Fire Response Plan is contained in the Emergency Operations Plan, Chapter XX, Paragraph XXX.  The Plan addresses MTF-wide fire and area-specific responses.  The Safety Manager reviews and updates the Fire Response Plan as often as needed and at least every year.

h.	Staff Roles.  At least annually, supervisors provide staff with department-specific training and education on –

(1) 	Actions (i.e., RACE/code) they must take at and away from a fire’s point of origin

(2) 	When and how to sound the fire alarm

(3) 	How to contain smoke and fire

(4) 	How to use a fire extinguisher

(5) 	Evacuation procedures and the location of areas of refuge

(6) 	Transfer of patients to areas of refuge and preparation for building evacuation

Training attendance is documented in the staff competency files.

i.	Fire Drills.

(1) 	The Safety Manager conducts and documents fire drills, according to the Fire Response Plan.

(2) 	Fire drills are conducted quarterly on all shifts in hospitals and ambulatory care and annually

(12 months from the date of the last drill) in business occupancies.

(3) 	At least 50% of the required drills are unannounced.

(4) 	Staff in all areas of every building where patients are housed or treated participates in drills to the extent called for in the fire plan.

(5) 	Each department is responsible for critiquing staff response to the fire drill, identifying deficiencies and opportunities for improvement and providing a copy of the after action report to the Safety Manager within three working days of the date of the drill.

(6)	 The Safety Manager reviews the fire drill after action reports to identify fire safety trends related to problems, deficiencies, and failures; recommends corrective actions; and presents summary information to the Safety Committee for review and action as needed.

j.	Preventive Maintenance for Fire Safety Equipment and Building Features.

- The Facility Manager maintains operational plans which provide guidance for the maintenance, testing, and inspection procedures for the fire protection systems.  The scheduled tests are summarized in

Appendix C.

(2)	All life safety equipment included in the Preventive Maintenance Program (PMP) is assigned a unique identification number and a corresponding record is created in the Defense Medical Logistics Standard Support (DMLSS) System database.  The identification numbers attach each component to a specific preventive maintenance procedure, schedule and service history file.

(3)	The MTF maintains documentation in the DMLSS database for the following:

(a) 	A current, accurate, and separate inventory of life safety equipment included in this management plan.

(b) 	Performance and safety testing of each critical component identified in the plan before initial use.

(c)	Critical components of life support utility systems/equipment consistent with maintenance strategies.

(4)	The PMP facilitates program implementation and time management, and it serves as a tracking tool to ensure that required inspections, tests, and maintenance, are performed, completed in a timely manner, and properly documented.

(5)	The Facilities Quality Control Manager randomly selects about 3% of the equipment having undergone preventive maintenance, inspects the chosen equipment, and compares his findings with those of the operator who originally inspected the equipment.  Appropriate action is taken whenever discrepancies occur.

k.	LSC Compliance.

(1)	Newly constructed and existing buildings are designed and maintained to comply with the NFPA 101, LSC; UFC 4-510-01, Design Medical Military Facilities; FGI Guidelines for Design and Construction of Healthcare Facilities; and the Americans with Disabilities Act and Architectural Barriers Act Accessibility Guidelines.

(2)	The Facility Manager prepares an electronic Statement of Conditions (e-SOC) compliance document for all hospital and ambulatory care buildings.  The Facility Manager is a registered Professional Engineer and has 20 years experience with LSC compliance.

(3)	The Facility Manager makes sure that sufficient progress is made towards completing corrective actions in a timely manner.  The Facility Manager develops the plans for improvement (PFI) or obtains equivalencies from the Joint Commission when buildings do not comply with the LSC.  If required, the PFI will include all of the following:

(a)  	Corrective actions

(b)  	Total cost of corrective actions

(c) 	Estimated completion date

(d) 	Documentation of ILSMs to be implemented

(4)	The Facility Manager uses a Building Maintenance Program to manage life safety equipment that is subject to routine failure.  The program includes processes for establishing inspecting and testing frequencies, data collection and analysis, program evaluation for effectiveness, and program improvement.  The following life safety equipment is included in the Building Maintenance Program:

(a)		Smoke and fire doors

(b)		Linen/trash chute doors

(c)		Smoke and Corridor Walls

(d)		Exit signage

(e)		Egress lighting

(f)		Grease producing devices

l.	Interim Life Safety Measures (ILSM).  The Facility Manager implements and documents ILSM to temporarily compensate for hazards posed by significant life safety deficiencies and construction.  Responsibilities, selection, and procedures for documenting implementation are provided in the Interim Life Safety Measures Policy No. XXX.

m. 	Orientation and Annual Refresher Education and Training Program.

(1)	The orientation and education component pertaining to fire safety addresses the following criteria:

(a)	Fire safety hazards in the MTF environment and assigned work area, such as building compartmentalization and defend in place policies; evacuation procedures and routes; location of evacuation equipment, fire extinguishers and medical gas shut-off valves; and the methods for eliminating or minimizing risk.

(b)	General fire safety processes, such as fire prevention; actions necessary to contain smoke and fire; storing combustibles, flammables, and compressed gases; electrical safety; and procedures for reporting unsafe/unhealthy working conditions.

(c)	Emergency processes such as reporting/responding to a fire.

(2)	The Chief, Plans, Training, Mobilization, and Security (PTMS) manages the organization-wide New Employee Orientation Program.  Generally, new employees are scheduled to attend orientation within 30 days of hire.

(3)	The Chief, PTMS also manages the Annual Refresher Training Program.  Generally, all staff and personnel attend annual refresher training during their birth month.

(4)	Supervisors provide worksite-specific orientation and annual refresher training.

(5)	All training is documented in the staff competency folders.

n.	Information Collection and Evaluation System.

1.	Reporting and Investigating Accidents, Injuries, Property Damage, Problems, Failures, and Use Errors.

(a)	The Incident Reporting/Investigation System covers all incidents involving equipment and property damage; occupational illness; and patient, personnel, or visitor injury.

(b) 	Supervisors must investigate all incidents and submit the appropriate incident report form

(DA Form 285, CA-1/CA-2, and DA Form 4106) to the Safety Manager, Patient Safety Manager, or Risk Manager within 3 working days of the occurrence.

(c)	The Safety Manager, Patient Safety Manager, Risk Manager, or other MTF representatives as deemed appropriate by the Commander promptly review incident reports to identify trends, determine root cause(s), and suggest corrective actions to prevent recurrence.  The Safety Manager, Patient Safety Manager, and Risk Manager prepare summary reports and submit them to the appropriate committee for further review and resolution as needed.

2.	Annual Evaluation.

(a)	The Safety and the Facility Managers keep the management plan current by reviewing the plan at least annually (i.e., one year from the date of the last review, plus or minus 30 days) and making necessary modifications based on the results of the evaluation and changes to policies, regulations, and standards.  In performing the annual review, they use a variety of sources such as inspection and audit results, accident/incident reports, employee reports of unsafe or unhealthy working conditions, customer satisfaction surveys, suggestion boxes, performance improvement committees, and other statistical information and tracking reports.  They may also use other forms of review and input from relevant sources, such as leadership, other EC/PE disciplines, management, staff, personnel, and volunteers.

(b)	The annual evaluation includes an assessment of the plan’s –

(1) 	Scope.  Based on the current locations and services offered, the scope of the plan is expanded, reduced or maintained at its present scope (buildings, equipment, people, operations, services).

(2) 	Objectives.  An annual assessment is made to determine if the objectives, as outlined in paragraphs

2.a through 2.d are current.

(3) 	Performance.  An acceptable level of performance is determined by the achievements related to the fire safety processes necessary for maintaining a successful Fire Safety Program.

(4) 	Effectiveness.  An acceptable level of effectiveness is determined by attaining success in meeting objectives and producing a satisfactory level of performance.

(c)	After the Safety/EC Committee approves the annual review, the results are submitted to the Executive Committee for review and approval.

(d)	The annual review is used as an opportunity to develop or modify programs, SOPs, and policies; identify and implement additional or more effective controls; and enhance the Employee Orientation and Annual Refresher Training Programs.

3.	Safety/EC Committee.  The Safety and Facility Managers are standing members of the Safety/EC Committee and are responsible for providing recurring reports on the status of the Fire Safety Management Plan to include:

(a) 	Annual evaluation of the Fire Safety Management Plan

(b) 	Performance improvement standards/initiatives

(c) 	Fire safety equipment preventive maintenance status reports

(d) 	Summary of fire drill after action reports

(e) 	Status of the e-SOC and PFIs

(f) 	Summary reports of ILSMs

(g) 	Deficiencies, problems, failures, and user errors

(h) 	Risk assessments

4. 	Performance Improvement Activities.

(a)	Performance monitoring is used to –

(1)  	Identify areas of concern and strengths in the MTF’s Fire Safety Program

(2)	Identify or determine actions necessary to address areas of concern

(3)	Assess actual compliance with relevant fire safety standards

(b)	The Safety Manager and Facility Managers –

(1) 	Identify at least one measurable performance improvement standard regarding actual or potential risk related to one or more of the following –

(a) 	Staff knowledge and skills

(b) 	Level of staff participation

(c) 	Monitoring and inspection activities

(d) 	Emergency and incident reporting

(e) 	Inspection, preventive maintenance, and testing of equipment

(2)	Consider high-risk, high-volume or chronic problems when developing performance standards to better focus limited resources.

(3)	 Set desired goals or benchmarks and develops and implements data collection and reporting procedures.

(4) 	Appendix D lists the Fire Safety Performance Measure(s) for this year.

(c)	The Safety/EC Committee tracks performance and documents the results in the committee minutes.

Commander

Deputy Commander for Nursing

Deputy Commander for Administration

Safety Manager

Logistics/Facilities

Safety/EC Committee

Installation Fire Department

Patient Safety Officer

Plans, Training, Mobilization, and Security

| Regulation, Policy, or SOP Number | Regulation, Policy, or SOP Name | Date Published | Point of Contact | Relevant EC Standard and Element of Performance |
| --- | --- | --- | --- | --- |

| System | Equipment | Frequency | Standards |
| --- | --- | --- | --- |
| Fire Detection and Alarm Systems | Supervisory signal devices listed in NFPA 7-7.2.1, except valve tamper switches | Quarterly (Annually if a Smart System is installed) | - NFPA 101, LSC, Section 7-6 - NFPA 25, Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems - NFPA 70, National Electrical Code - NFPA 72, National Fire Alarm Code |
|  | Water flow devices | Quarterly |  |
|  | Valve tamper switches | Semi-annually |  |
|  | Duct detectors | Annually |  |
|  | Electromechanical releasing devices | Annually |  |
|  | Heat detectors | Annually |  |
|  | Manual fire alarm boxes | Annually |  |
|  | Smoke detectors | Annually |  |
|  | Occupant alarm notification devices (audible and visible devices) | Annually |  |
|  | Off-premises emergency forces notification and transmission equipment | Quarterly |  |
| Water-based Automatic Fire Extinguishing Systems | Fire pumps | Weekly, no flow condition | - NFPA 13, Installation of Sprinkler Systems - NFPA 14, Standpipe and Hose Systems - NFPA 20, Centrifugal Fire Pumps - NFPA 25, Water-Based Fire Protection Systems - NFPA 1962, Fire Hose Care, Use |
|  | Fire pumps | Annually, flow condition |  |
|  | Main drains | Annually, an all system risers |  |
|  | Fire department connections | Quarterly |  |
|  | Water storage tanks high and low water level alarms | Semi-annually |  |
|  | Water storage tanks low water temperature alarms (during cold weather only) | Monthly |  |
|  | Standpipe occupant hoses | Hydrostatically tested New – 5 years Existing – 3 years |  |
|  | Standpipe systems | Water flow tests at least every 5 years |  |
| Dry Chemical Suppression Systems | Kitchen automatic fire extinguishing systems | Semiannually | - NFPA 96, Commercial Cooking Operations - NFPA 12, Carbon dioxide Systems - NFPA 17, Dry Chemical Extinguishing Systems |
|  | Carbon dioxide and other automatic fire extinguishing systems | Annually |  |
| Portable Fire Extinguishers | Portable fire extinguishers | Inspected monthly Maintained annually | - NFPA 10 |
| Smoke and Fire Management Systems | Smoke and fire dampers | Operated for full closure, 1 year after installation and every 6 years thereafter | - NFPA 80, Fire Doors and Fire Windows - NFPA 105, Standard for the Installation of Smoke Door Assemblies and Other Opening Protectives |
|  | Automatic smoke detection shutdown devices for air handling equipment | Annually |  |
|  | Sliding and rolling fire doors | Annually |  |

| Performance Objective | Performance Indicator(s) | SMART Performance Measure/ Action Plan |
| --- | --- | --- |
| Effectively manage fire safety risks by using best industry practices. Specifically, managing risk through the prompt correction of Life Safety Code (LSC) deficiencies. (BSC: Internal Processes) | % LSC deficiencies corrected ≤ 45 days | - What is your goal? - Is it measurable? - SMART performance measure - What constraints do you have (time, money, other resources)? - What are the steps you will take to meet your goal? - How will you prioritize these steps? - What data do you need to collect? - How will you collect and report the data? |
| Optimize resources by using efficient fire safety processes and lifecycle management of facilities. Specifically, proactively reducing the number of LSC deficiencies occurring throughout the year. (BSC: Resources) | # New LSC deficiencies, failures, problems detected each quarter | - What is your goal? - Is it measurable? - SMART performance measure - What constraints do you have (time, money, other resources)? - What are the steps you will take to meet your goal? - How will you prioritize these steps? - What data do you need to collect? - How will you collect and report the data? |
| Improve staff performance through effective fire safety security education and training. Specifically, increase staff knowledge of emergency procedures. (BSC: Learning and Growth) | % Staff who know how to properly use a fire extinguisher | - What is your goal? - Is it measurable? - SMART performance measure - What constraints do you have (time, money, other resources)? - What are the steps you will take to meet your goal? - How will you prioritize these steps? - What data do you need to collect? - How will you collect and report the data? |
| Improve staff and patient satisfaction by providing a safe physical environment. Specifically, reduce the number complaints resulting from false alarms. (BSC: Customer Satisfaction) | # staff complaints regarding false alarms | - What is your goal? - Is it measurable? - SMART performance measure - What constraints do you have (time, money, other resources)? - What are the steps you will take to meet your goal? - How will you prioritize these steps? - What data do you need to collect? - How will you collect and report the data? |