ENVIRONMENT OF CARE

UTILITY SYSTEMS MANAGEMENT PLAN

JANUARY 2013

1.	Goal

2.	Objectives

3.  	Scope

4.	Responsibilities

5.  	Utility Systems Elements of Performance

a.	Utility Systems Management Plan

b.	Risk Assessments

c.	Risk Management

d.	Design and Installation of the Utility 			Systems

e.	Utility System Inventory

f.	Preventive Maintenance Strategies

g.	Preventive Maintenance Intervals

h.	Cooling towers

i.	Ventilation Systems

j. 	Utility Systems Distribution

k.  	Labeling for Emergency Shutdown

l.  	Utility System Disruption 					Procedures

m.	Shutting Down Malfunctioning Systems

n.	Emergency Clinical Procedures

o.	Emergency Repairs

p.	Emergency Response

q.  	Emergency Electrical Power

r.  	Inspections, Tests, and Maintenance

(1) Initial Testing

(2) Life Support

(3) Infection Control

(4) Non Life Support

s.	Emergency Electrical Power

t.	Medical Gas and Vacuum 					Systems

u.	Orientation and Education Program

v.	Information Collection and 					Evaluation System

(1) Incident Reporting and 					Investigating

(2) Annual Evaluation

(3) Safety/EC Committee

(4) Monitoring of Performance

1.	Goal.  This management plan describes the framework to manage risks associated with utility systems and to improve program performance.  The scope and objectives are consistent with the Command’s values, vision, and mission to provide quality healthcare to Soldiers, retirees, and their families.

2.	Objectives.  The following objectives will ensure the physical safety of patients, visitors, and staff and prevent the loss of property.

a.	Effectively manage utility system risks by using best industry practices

b.	Optimize resources by using efficient utility system processes and lifecycle management of equipment

c.	Improve staff performance through effective utility system education and training

d.	Improve staff and patient satisfaction by providing a safe physical environment

3.	Scope.

a.	The plan applies to this Military Treatment Facility (MTF) and all subordinate MTFs to include (LIST CLINICS AND SATELLITE LOCATIONS SERVED BY THE MTF AND COVERED UNDER THIS PLAN).

b.	The utility systems covered under this plan are: electrical distribution; emergency power; horizontal and vertical transport (elevators and pneumatic tube system); heating, ventilating, and air- conditioning; plumbing; boiler and steam; medical gases; medical/surgical vacuum; and communication systems (nurse call, overhead paging, computer, and telephone).

4.	Responsibilities.

a.	The Facility Manager develops, implements, and monitors this plan and the MTF’s Utility System Maintenance Regulations.

b.	The Chief, Information Management inspects, tests, and maintains the communication systems.

c.	The (INSTALLATION) Department of Public Works inspects, tests, and maintains the (LIST) systems.

d.	The (CONTRACTOR NAME) inspects, tests, and maintains the (LIST) systems.

e.	The Organization Chart in Appendix A shows the primary officers, departments, and services that provide input into the development, implementation, and maintenance of the Utility Systems Program.

f.	All staff must be trained and competent in safe operation and use of utility systems and in emergency response and reporting procedures.

5.  	Utility Systems Elements of Performance.  The Reference Crosswalk in Appendix B lists the corresponding policies, regulations, SOPs, systems, and databases pertaining to each of these requirements.

a.	Utility Systems Management Plan.  This management plan is based on a plan, teach, implement, respond, monitor, and improve framework, and it addresses the essential process for making sure that all utility systems are safe and functional.

b.	Risk Assessments.

(1) 	The utility system risk assessment process focuses on the impact of utility system components on the MTF’s life support, infection control, environmental support, equipment support, and communication systems.

(2)	Both proactive risk assessments (e.g., internal performance improvement data; staff, patient, and family feedback; environmental monitoring; results of failure mode and effects analyses; governmental regulation reviews; association, society, and professional literature reviews; exercise after action reports; preventive maintenance; and design reviews; etc.) and reactive risk assessments (incident investigations, utility system failure investigations, root cause analyses, etc.) are used to identify trends for which corrective action is needed.

(3)	The risk assessment process is also used to manage “gray areas” that do not have a clear resolution.  An example of a “gray area” is deciding the best way to secure sharps in the Emergency Room.  “Gray area” issues are brought to the Safety/EC Committee for discussion and resolution.

c.	Risk Management.

(1)	Facility personnel work with supervisors and staff to exchange information and educate each other on any risks associated with the utility systems.  First-line supervisors make sure users understand the application, safe operation, and emergency procedures for the utility systems located in their work areas.

(2) The Facility Manager evaluates, tracks, and abates all risks associated with the utility systems on a worst-first basis.  Interim measures are implemented when hazards cannot be immediately abated to manage risk and minimize potential harm to patients, staff, and visitors.

d.	Design and Installation of the Utility Systems.  The Facility Manager uses the Department of Defense Medical Military Construction Program Facilities Design and Construction Criteria, UFAS 4-510-01, 16 October 2003; AIA Guidelines for Design and Construction of Hospital and Healthcare Facilities; Americans with Disabilities Act and Architectural Barriers Act Accessibility Guidelines, July 23, 2004; and a number of other standards listed in Appendix C to make sure that the utility systems meet the patient care and operational needs of the services in the MTF’s buildings.

e.	Utility System Inventory.

(1) 	All utility systems having an impact on the environment, life support, infection control, support of the environment, equipment, and communications are classified as critical systems and they are included in the inventory.  Newly acquired equipment is added to the inventory within three months of acquisition/installation.

(2) 	All systems or components included in the Preventive Maintenance Program are assigned a unique identification number and a corresponding record is created in the Defense Medical Logistics Standard Support (DMLSS) System database.  The identification numbers attach each component to a specific preventive maintenance procedure, schedule, and service history file.

(3) 	The on-time maintenance completion rate for all critical operating components for life support utility systems is 100 percent.  The expected on time maintenance completion rate for all critical operating components for non life support utility systems, is at or better than

95 percent.

(4) 	The DMLSS database is used to maintain documentation for the following:

(a) 	A current, accurate, and separate inventory of utility components included in the utility management plan.

(b) 	Performance and safety testing of each critical component identified in the plan before initial use.

(c)	Critical components of life support utility systems/equipment consistent with maintenance strategies.

(d) 	Critical components of infection control utility systems/equipment for high-risk patients.

(e)	Critical components of non-life support utility systems/equipment.

f.	Preventive Maintenance Strategies.  Facility personnel use a variety of maintenance strategies to include:

(1) 	Interval-based maintenance (e.g., adding chemicals to cooling towers, lubricating parts, etc.).

(2) 	Predictive maintenance (e.g., infrared scans of electrical systems, ultrasonic scans of pumps, oil analysis for diesel generators, etc.).

(3) 	Metered maintenance (e.g., compressors maintained based on the number of hours run).

(4) 	Corrective maintenance (e.g., run to fail maintenance on non critical systems).

(5) 	The Facilities Manager may modify maintenance intervals based on MTF experience and risk levels associated with the system’s function, clinical area that it supports, and its incident history with the Safety/EC Committee’s approval.

g.	Preventive Maintenance Intervals.

(1) 	The DMLSS data base serves as a tracking tool to document completion of required inspections, tests, and maintenance.  Each month the DMLSS database automatically generates scheduled services requirements based on the maintenance types described in Paragraph 5.f. above.

(2) 	Each month the Facilities Quality Control Manager randomly selects 3 percent of the equipment having undergone maintenance, inspects the chosen equipment, and compares the findings with the maintenance worker’s (who originally maintained the equipment) findings.  Appropriate action is taken whenever discrepancies occur.

h.	Cooling Towers and Water Systems.

(1)	Facility personnel follow the guidance in ASHRAE 12-2000 and the CDC Guidelines for Environmental Infection Control in Healthcare Facilities to control pathogenic biological agents (i.e., Legionella) in hot, cold, and aerosolizing water systems and cooling towers.

(2)	If there is a case of suspected or known hospital-acquired infection, the Facility Manager works together with Infection Control and Preventive Medicine to review engineering policies and procedures related to inspections, preventive maintenance, and the culturing guidelines to be used.

(3) 	All inspections, tests and maintenance are documented in the DMLSS database.

i.	Ventilation Systems.

(1)	Facility personnel use guidance from a number of references, such as the

UFC 4-510-01; ASHRAE; AIA Guidelines for Design and Construction of Hospitals and Health Care Facilities, CDC Guidelines for Preventing the Transmission of Mycobacterium tuberculosis in Health-Care Settings, 2005; etc. when designing, installing, and maintaining air handling and ventilation systems.  Emphasis is placed on the proper pressure relationships, air exchange rates, and filtration efficiencies in areas where patients are treated or housed that may have auto immune systems that are suppressed. These areas include operating rooms, special procedure rooms, delivery rooms, protective isolation rooms, laboratories and sterile supply rooms.

(2)	If there is a case of suspected or known hospital-acquired infection, the Facility Manager works together with Infection Control and Preventive Medicine to review engineering policies and procedures related to inspections, preventive maintenance, and the culturing guidelines to be used.

(3) 	All inspections, tests and maintenance are documented in the DMLSS database.

j. 	Utility Systems Distribution.  For each major system, Facility personnel maintain current, detailed schematics mapping the layout of each system.  These schematics show technical details and operational procedures.  These documents also include distribution and controls for partial or complete shutdown as well as operating procedures for key controls to include notification of staff in affected areas.

k.  	Labeling for Emergency Shutdown.  Emergency shut off controls are labeled for a partial or complete emergency shutdown, and the labels are inspected at least annually.

l.  	Utility System Disruption Procedures.

(1) 	When planned utility outages are required for repairs, maintenance or construction, facility personnel notify the affected departments and services at least seven days in advance of the scheduled start date to avoid unexpected inconveniences, property damage, safety hazards, or loss of information or research.

(2) 	Staff immediately reports loss of a utility system to the Facilities Department via telephone when unplanned utility outages occurs as the result of a repair, maintenance, or construction activity or other natural/man made event.

m.	Shutting Down Malfunctioning Systems.  Emergency shutdown and notification/contingency plans for utility system disruptions are addressed in the Facilities Operational Plans and in the Emergency Operation Plan (EOP).  Examples of emergency procedures include, but are not limited to –

(1)	Shutdown/Loss of Electricity (see Chapter XX, Annex XX of the EOP)

(2)	Shutdown/Loss of Water (see Chapter XX, Annex XX of the EOP)

(3)	Shutdown/Loss of heating, ventilation, and air conditioning (see Chapter XX, Annex XX of the EOP)

(4)	Shutdown/Loss of piped medical gases (see Chapter XX, Annex XX of the EOP)

(5)	Shutdown/Loss of steam/boilers (see Chapter XX, Annex XX of the EOP)

(6)	Shutdown/Loss of communications (see Chapter XX, Annex XX of the EOP)

(7)	Shutdown/Loss of chilled water/chillers (see Chapter XX, Annex XX of the EOP)

(8)	Shutdown/Loss of natural gas/oil (see Chapter XX, Annex XX of the EOP)

(9)	Shutdown/Loss of elevators (see Chapter XX, Annex XX of the EOP)

n.	Emergency Clinical Procedures.  Facility personnel and Department of Nursing develop emergency procedures for utility system disruptions which address the following:

(1) 	Specific procedures in the event of utility systems malfunction

(2) 	Identification of an alternate source of essential utilities

(3) 	Shutoff of malfunctioning systems and notification of staff in affected areas

(4) 	Procedures for obtaining repair services when utility systems fail

o.	Emergency Repairs.  See Paragraph 5.m. above.

p.	Emergency Response.  See Paragraphs 5.m. and 5 n. above.

q.  	Emergency Electrical Power.  The MTF has (List quantity and size) emergency generators.  The emergency power source supplies electricity to the following:

(1)	Alarm systems

(2) 	Exit route illumination

(3) 	Emergency communication systems

(4) 	Illumination of exit signs

(5) 	Blood, bone, and tissue storage units

(6) 	Emergency/urgent care areas

(7) 	Elevators (at least one for non ambulatory patients)

(8) 	Medical air compressors

(9)  Medical and surgical vacuum systems

(10) Areas where electrically powered life-support equipment is used

(11)  Operating rooms

(12)  Postoperative recovery rooms

r.  	Inspections, Tests, and Maintenance.

(1)	 Initial.  Facility personnel test all systems prior to initial use and annually unless otherwise specified by the preventive maintenance frequency defined in the DMLSS database.

(2) 	Life Support.  See Paragraphs 5.e, 5.f, and 5.g.

(3) 	Infection Control.  See Paragraphs 5.e, 5.f, and 5.g.

(4) 	Non Life Support.  See Paragraphs 5.e, 5.f, and 5.g.

s.  	Emergency Power Supply Systems.

(1) 	Facility personnel test battery-powered lights for egress purposes for 30 seconds every 30 days, and for 1½ hours annually.

(2) 	The MTF does not have and stored emergency power supply systems.

(3) 	Facility personnel test the emergency power system twelve times a year at intervals of not less than 20 days and not more than 40 days.  Testing is conducted for at least 30 continuous minutes under a dynamic load that is at least 30% of the nameplate rating of the generator.  Generators that are tested to less than the 30% of the nameplate rating still require a 30 minute testing period.  Guidance for testing generators that tested less than the nameplate rating and for diesel-powered generators that do not meet the minimum exhaust gas temperatures is located in the JC EC Standard EC.02.05.07.

(4)	All transfer switches are tested 12 times annually with the testing intervals not less than 20 days and not more than 40 days apart.

(5) 	Facility personnel further test each emergency generator at least once every

36 months for a minimum of four continuous hours.  The test is conducted under a load (dynamic or static as necessary) that is at least 30% of the nameplate rating of the generator.

(6)  	If a test of an emergency power supply system fails, facility personnel implement interim measures to compensate for the risk to patients, visitors, and staffs until necessary repairs or corrections are completed, and they perform a retest after making the necessary repairs or corrections.

(7) 	All inspections, tests, and maintenance are documented in the DMLSS database.

t.	Medical Gas and Vacuum Systems.

(1)	The medical gas system includes compressed air for medical and dental patient and laboratory use; vacuum for medical and dental patient use, laboratory dust collection, and waste anesthesia gas disposal; and gases for patient, laboratory, and equipment use. The system design includes centralized gas storage, compressors, a piped distribution system, and connection outlets.  Point-of-use or decentralized systems are also included.

(2)	Facility personnel follow the guidance in NFPA 99 to install and test the medical gas system. Testing includes, but is not limited to, cross-connection, purity, pressure, and alarm testing.  All testing and certification of the medical gas systems is done by an independent testing agency.

(3) All inspections, tests and maintenance are documented in the DMLSS database.

(4) Facilities follows the guidance in NFPA 99 to label all piped medical gas and vacuum systems main supply valves and area shutoff valves.

u.	Orientation and Education Program.

(1)	The orientation and education component pertaining to utility systems addresses the following criteria:

(a) 	Staff.

(1) 	The utility system's capabilities, limitations, and special applications

(2) 	Emergency procedures in the event of system failure

(3) 	Location and instructions for use of emergency shutoff controls

(4) 	Processes for reporting utility system management problems, failures, and user errors

(b) 	Maintenance workers.

(1) 	Certification, license or information and skills necessary to perform assigned maintenance responsibilities

(2) 	The utility system's capabilities, limitations, and special applications

(3)	Emergency procedures in the event of system failure

(4) 	Location and instructions for use of emergency shutoff controls

(5) 	Processes for reporting utility system management problems, failures, and user errors

(6) 	Shop safety (lockout/Tagout, confined spaces, tool and ladder safety, etc.)

(2)	The Chief, Plans, Training, Mobilization, and Security (PTMS) Office, manages the organization-wide New Employee Orientation Program.  Generally, new employees are scheduled to attend orientation within 30 days of hire.

(3)	The Chief, PTMS Office manages the Annual Refresher Training Program.  Generally, all staff and personnel attend annual refresher training during their birth month.

(4)	Supervisors provide worksite-specific orientation and annual refresher training.

(5)	All training is documented in the staff competency folders.

v.	Information Collection and Evaluation System.

(1) 	Incident Reporting and Investigating.

(a)	The Facility Manager identifies, documents, investigates, and evaluates utility system incidents, failures, problems, or user errors to identify trends and problems that pose a potential threat to health and safety and opportunities for improvement.  Investigations may include a review of equipment service reports, incident reports, utility failures, and user errors.  Corrective actions are implemented in a timely manner and the results are evaluated for effectiveness.

(b)	Typical incidents that require reporting and investigation include normal electric power system failures, emergency power system failures, water system failures or contamination, steam system failures, sewer system leaks and major blockages, medical gas system failures, disruption of HVAC service to patient care units and service areas, and any other incident deemed appropriate by the Facility Manager.

(2) 	Annual Evaluation.

(a)	The Facility Manager keeps the management plan current by reviewing the plan at least annually (i.e., one year from the date of the last review, plus or minus 30 days) and making modifications based on changes to policies, regulations, and standards.  In performing the annual review, the Facility Manager uses a variety of sources such as inspection and audit results, accident/incident reports, employee reports of unsafe or unhealthy working conditions, customer satisfaction surveys, suggestion boxes, performance improvement committees, and other statistical information and tracking reports.  The Facility Manager may also use other forms of review and input from relevant sources such as leadership, other EC/PE disciplines, management, staff, personnel, and volunteers.

(b)	The annual evaluation includes an assessment of the plan’s:

(1) 	Scope.  Based on the outcome of objectives assessment, the scope of the plan is expanded, reduced or maintained at its present scope (buildings, equipment, people, operations, services)

(2) 	Objectives.  An annual assessment is made to determine if the objectives, as outlined in paragraphs 2.a through 2.d are current.

(3) 	Performance.  An acceptable level of performance is determined by the achievements related to the utility management processes necessary for maintaining a successful Utility Management Program.

(4) 	Effectiveness.  An acceptable level of effectiveness is determined by attaining success in meeting objectives and producing a satisfactory level of performance.

(c)	Once the Safety/EC Committee approves the annual review, the results are submitted to the Executive Committee for review and approval.

(d)	The annual review is used as an opportunity to develop or modify programs, plans, and policies; identify and implement additional or more effective controls; and enhance the Employee Orientation and Annual Refresher Training Programs.

(3) 	Safety/EC Committee.  The Facility Manager is a standing member of the Safety/EC Committee and is responsible for coordinating, documenting, and presenting information related to the utility systems to the committee.  In addition, the Facility Manager is responsible for providing recurring reports on the status of the Utility Systems Management Plan to include:

(a) 	Annual evaluation of the Utility Systems Management Plan

(b) 	Performance Improvement Standards/initiatives

(c) 	Risk assessments

(d) 	Outages, failures, user errors

(e) 	Status of the Testing/Inspecting/Maintenance Program

(f) 	Construction Risk Assessments

(4) 	Monitoring of Performance.

(a)	Performance monitoring is used to –

(1)	Identify areas of concern and strengths in the MTF’s Utility Systems Program

(2)	Identify or determine actions necessary to address areas of concern

(3)	Assess actual compliance with relevant standards

(b)	The Facility Manager –

(1) 	Identifies at least one measurable performance improvement standard regarding actual or potential risk related to one or more of the following:

(a) 	Staff knowledge and skills

(b) 	Level of staff participation

(c) 	Monitoring and inspection activities

(d) 	Emergency and incident reporting

(e) 	Inspection, preventive maintenance, and testing of equipment

(2)  	Considers high-risk, high-volume or chronic problems when developing performance standards to better focus limited resources.

(3)  	Sets desired goals or benchmarks and develops and implements data collection and reporting procedures.

(4)	Appendix D lists the Utility System performance measure(s) for this year.

(c)	The EC Committee tracks performance and documents the results in the committee minutes.

Commander

Deputy Commander for Administration

Deputy Commander for Nursing

Risk Manager

Safety/EC Committee

Logistics

Plans, Training, Mobilization, and Security

Facilities

Patient Safety Manager

Infection Control

Preventive Medicine

Industrial Hygiene

Safety Manager

Information Management

| Regulation, Policy, or SOP Number | Regulation, Policy, or SOP Name | Date Published | Point of Contact | Relevant EC Standards and Elements of Performance |
| --- | --- | --- | --- | --- |

| System | Regulation, Code or Standard |
| --- | --- |
| Heating Ventilation and Air Conditioning | UFC 4-510-01 ASHRAE, NFPA 90A |
| Medical Gas System | UFC 4-510-01 NFPA 99 |
| Medical/Surgical Vacuum Systems | UFC 4-510-01 NFPA 99 |
| Electrical Distribution System | UFC 4-510-01 NFPA 70 |
| Emergency Power System | UFC 4-510-01,AIA Guidelines NFPA 110 |
| Elevators | UFC 4-510-01 ASME A17.1b (1998) This standard governs the installation, alteration, maintenance and testing of elevators and escalators. ASME A17.2.1b (1998) Inspector's Manual for Electric Elevators ASME A17.2.2a (1998) Inspector's Manual for Hydraulic Elevators ASME A17.2.3 (1998) Inspector's Manual for Escalators and Moving Walks ASME A17.3 (1996) Standard for Existing Elevators and Escalators ASME A90.1 (1997) Standard for Belt Manlifts |
| Nurse Call System | UFC 4-510-01 |
| Telephone System | UFC 4-510-01 |
| Boiler/Steam | UFC 4-510-01 The Boiler and Pressure Vessel Code of the American Society of Mechanical Engineers (ASME), dated July 1, 1998 and addenda and interpretations through December 31, 1998. 1998 Edition of the ANSI/ASME B31.1, Power Piping Code and Addenda; 1996 Edition of the ANSI/ASME B31.9, Building Service Piping; 1998 Edition of the National Board Inspection Code ANSI/NB 23 1998 Edition of ASME (CSD-1), Controls and Safety Devices |
| Plumbing | UFC 4-510-01 1997 Uniform plumbing code with state amendments. This code is used for all commercial plumbing code applications. |
| HVAC | UFC 4-510-01 AIA Guidelines for Design and Construction of MTFs and Healthcare Facilities OSHA CPL.2.106, Enforcement Procedures and Scheduling for Occupational Exposure to Tuberculosis |
| Aerosolizing Water Systems | ASHRAE 12-2000 CDC Guidelines for Environmental Infection Control in Healthcare Facilities |

| Performance Objective |  | Performance Indicator(s) |  | SMART Performance Measure/ Action Plan |
| --- | --- | --- | --- | --- |
| Effectively manage utility system risks by using best industry practices. (BSC: Internal Processes) |  | # Minutes required to respond to trouble calls % Preventive maintenance, checks, calibration completed on time # Successful emergency generator tests conducted within prescribed time frames # Utility System Failure resulting in patient injury each quarter |  | - What is your goal? - Is it measurable? - SMART performance measure - What constraints do you have (time, money, other resources)? - What are the steps you will take to meet your goal? - How will you prioritize these steps? - What data do you need to collect? - How will you collect and report the data? |
| Optimize resources by using efficient utility system processes and lifecycle management of facilities. (BSC: Resources) |  | % man-hours applied to scheduled work # Utility system problems, failures, and use errors resulting in patient disruption |  | - What is your goal? - Is it measurable? - SMART performance measure - What constraints do you have (time, money, other resources)? - What are the steps you will take to meet your goal? - How will you prioritize these steps? - What data do you need to collect? - How will you collect and report the data? |
| Improve staff performance through effective utility system education and training. (BSC: Learning and Growth) | # of corrective maintenance activities resulting from user error or abuse |  | - What is your goal? - Is it measurable? - SMART performance measure - What constraints do you have (time, money, other resources)? - What are the steps you will take to meet your goal? - How will you prioritize these steps? - What data do you need to collect? - How will you collect and report the data? |  |
| Improve staff and patient satisfaction by providing a safe physical environment. (BSC: Customer Satisfaction | # Customer complaints received each quarter |  | - What is your goal? - Is it measurable? - SMART performance measure - What constraints do you have (time, money, other resources)? - What are the steps you will take to meet your goal? - How will you prioritize these steps? - What data do you need to collect? - How will you collect and report the data? |  |